CW-P-241B Maintenance Work Orders and Closeout Notes

Site: West Cooling Water Pump House | Package: CW-SKID-241 | Revision: maintenance closeout pack | Date range: 2026-06-10 to 2026-06-18.

# 1. Work order register

| work_order | date_closed | tag_used | scope | closeout_status | controlling_note |
| --- | --- | --- | --- | --- | --- |
| WO-77481 | 2026-06-14 | CW-P-241B | Mechanical seal replacement and impeller inspection | CLOSED | Impeller trim measured at 288 mm during casing inspection; old register trim 292 mm not revalidated. |
| WO-77482 | 2026-06-15 | P-241B | Laser alignment and soft-foot correction | CLOSED | Final alignment accepted using 112 mm coupling spacer; soft-foot residuals all below 0.05 mm. |
| WO-77483 | 2026-06-16 | CW-P-241B | Seal flush conversion verification | CLOSED | Field line tracing confirms Plan 11 internal recirculation; Plan 32 plate left on old register tag is not current. |
| WO-77484 | 2026-06-17 | CW-P-241B | Post-maintenance run test and operations handover | CLOSED WITH MONITOR | Raw flow display requires 0.973 calibration factor; vibration route requires continued trend watch. |
| WO-77485 | 2026-06-17 | CW-P-241 | Guard and housekeeping punch list | CLOSED | Alias CW-P-241 used in a shop note; work applied to CW-P-241B only. |

# 2. Component observations

| component | observed_value | units | source_detail | acceptance_note |
| --- | --- | --- | --- | --- |
| Impeller trim | 288 | mm | WO-77481 casing inspection line 4 | Consistent with borescope range 288-289 mm. |
| Seal flush | Plan 11 | plan | WO-77483 line tracing | Supersedes Plan 32 register plate. |
| Coupling spacer | 112 | mm | WO-77482 alignment setup | Matches laser alignment report setup. |
| Soft foot maximum | 0.03 | mm | WO-77482 final soft-foot record | Below 0.05 mm tolerance. |
| Run-test flow | raw display only | gpm | WO-77484 operator entry | Must be corrected with calibration factor. |

# 3. Handover cautions

The run-test note labels the pump as OK, but the technician closeout states that raw flow cannot be accepted without the 0.973 meter factor. The vibration route remains a separate condition trend and does not override nameplate, alignment, or geometry records.

# 4. Reconciliation flags for technician review

| flag_id | issue | conflicting_source | preferred_basis |
| --- | --- | --- | --- |
| WO-FLAG-01 | Impeller trim conflict | Asset register 292 mm | Work order and field survey indicate 288-289 mm. |
| WO-FLAG-02 | Seal flush conflict | Asset register Plan 32 | Work order and line tracing show Plan 11. |
| WO-FLAG-03 | Coupling spacer conflict | spare quote 108 mm | Installed survey and alignment setup show 112 mm. |
| WO-FLAG-04 | Tag alias conflict | CW-P-241 shorthand | Normalize to CW-P-241B. |